## RCO #1
IBI Residential Load Calculation Worksheet
Worksheet # 1
Revised 03/01/24
Conditions: Single family dwelling, heating load is larger than air-conditioning load.
(Heat Pump and/or Electric Space Heating)
(Based on NEC 220.82)
Existing plus Added Loads (less HVAC)
| sq. ft. @ 3 watts sq. ft | [6 empty] | 0 | watts
| Small Appliance Circuits @ 1500 watts ea. (Minimum 2) | [6 empty] | 0 | watts
| Laundry Circuit(s) @ 1500 watts ea. (Minimum is 1) | [6 empty] | 0 | watts
| Range (Nameplate Rating) | [6 empty] | 0 | watts
| Cooktop (Nameplate Rating) | [6 empty] | 0 | watts
| Oven (Nameplate Rating) | [6 empty] | 0 | watts
| Electric Water Heater | [6 empty] | 0 | watts
| Electric Clothes Dryer (Enter larger: 5000 Watts or Nameplate Rating) | [6 empty] | 0 | watts
| Dishwasher | [6 empty] | 0 | watts
| Disposal | [6 empty] | 0 | watts
| Sump Pump | [6 empty] | 0 | watts
| Sewage Pump | [6 empty] | 0 | watts
| Water Pump | [6 empty] | 0 | watts
| Microwave Oven | [6 empty] | 0 | watts
| Garage Door Opener | [6 empty] | 0 | watts
| EVSE (Enter larger: 7200 Watts or Nameplate Rating) | [6 empty] | 0 | watts
[8 empty] | 0 | watts
[8 empty] | 0 | watts
[8 empty] | 0 | watts
| Total Calculated Load (less HVAC) | [6 empty] | 0 | watts
Service Demand
General Load:
First 10kw of Total Calculated Load (less HVAC) @ 100% | [7 empty] | 0 | watts
Remainder of Total Calculated Load (less HVAC) @ 40% | [7 empty] | 0 | watts
Total General Load | [7 empty] | 0 | watts
HVAC Load:
| Nameplate Heat Pump Compressor load @ 100% | [6 empty] | 0 | watts
(Volts X Amps = Watts)
| Nameplate Electric Space Heating Load @ 65% | [6 empty] | 0 | watts
(Nameplate Rating in watts X .65) ((NEC 220.82 (C)(4)(5))
[8 empty] | 0 | watts
Total General Load |  |  | + | Total HVAC Load |  | = | Calculated Service Load
0 |  | watts | + | 0 | watts | = | 0 |  | watts
Calculated Service Load |  |  | ¸ | Service Voltage |  | = | Minimum Service Ampacity
0 |  | watts | ¸ | 240 | volts | = | 0 |  | amps
Note on B10: Minimum is 2
Note on B11: Minimum is 1
Note on B12: Nameplate Rating in watts (Volts x Amps = Watts
Note on B13: Nameplate Rating in watts (Volts x Amps = Watts
Note on B14: Nameplate Rating in watts (Volts x Amps = Watts
Note on B15: Nameplate Rating in watts (Volts x Amps = Watts
Note on B16: See *
Note on B17: Nameplate Rating in watts (Volts x Amps = Watts
Note on B18: Nameplate Rating in watts (Volts x Amps = Watts
Note on B19: Nameplate Rating in watts (Volts x Amps = Watts
Note on B20: Nameplate Rating in watts (Volts x Amps = Watts
Note on B21: Nameplate Rating in watts (Volts x Amps = Watts
Note on B22: Nameplate Rating in watts (Volts x Amps = Watts
Note on B23: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B24: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B25: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B26: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B27: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B37: (Volts)
Note on B38: (Amps)
Note on B39: Nameplate Rating in watts

## RCO #2
IBI Residential Load Calculation Worksheet | [7 empty] | Elect. Permit No.
Worksheet # 2
(Revised 03/01/24)
Conditions: Single family dwelling, air-conditioning load is larger than heating load.
(Based on NEC 220.82)
Existing plus Added Loads (less HVAC)
| sq. ft. @ 3 watts sq. ft | [6 empty] | 0 | watts
| Small Appliance Circuits @ 1500 watts ea. (Minimum is 2) | [6 empty] | 0 | watts
| Laundry Circuit(s) @ 1500 watts ea. (Minimum is 1) | [6 empty] | 0 | watts
| Range (Nameplate Rating) | [6 empty] | 0 | watts
| Cooktop (Nameplate Rating) | [6 empty] | 0 | watts
| Oven (Nameplate Rating) | [6 empty] | 0 | watts
| Electric Water Heater | [6 empty] | 0 | watts
| Electric Clothes Dryer (Enter larger: 5000 Watts or Nameplate Rating) | [6 empty] | 0 | watts
| Dishwasher | [6 empty] | 0 | watts
| Disposal | [6 empty] | 0 | watts
| Sump Pump | [6 empty] | 0 | watts
| Sewage Pump | [6 empty] | 0 | watts
| Water Pump | [6 empty] | 0 | watts
| Microwave Oven | [6 empty] | 0 | watts
| Garage Door Opener | [6 empty] | 0 | watts
| EVSE (Enter larger: 7200 Watts or Nameplate Rating) | [6 empty] | 0 | watts
[8 empty] | 0 | watts
[8 empty] | 0 | watts
[8 empty] | 0 | watts
[8 empty] | 0 | watts
| Total Calculated Load (less HVAC) | [6 empty] | 0 | watts
Service Demand
General Load:
First 10kw of Total Calculated Load (less HVAC) @ 100% | [7 empty] | 0 | watts
Remainder of Total Calculated Load (less HVAC) @ 40% | [7 empty] | 0 | watts
Total General Load | [7 empty] | 0 | watts
HVAC Load:
| Air Conditioning Load @ 100% (Volts X Amps = Watts) | [6 empty] | 0 | watts
| Furnace/Air Handler Load (Volts X Amps = Watts) | [6 empty] | 0 | watts
| Total HVAC Load | [6 empty] | 0 | watts
Total General Load |  |  | + | Total HVAC Load |  | = | Calculated Service Load
0 |  | watts | + | 0 | watts | = | 0 |  | watts
Calculated Service Load |  |  | ¸ | Service Voltage |  | = | Minimum Service Ampacity
0 |  | watts | ¸ | 240 | volts | = | 0 |  | amps
Note on B8: sq. ft.
Note on B9: Minimum is 2
Note on B10: Minimum is 1
Note on B11: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B12: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B13: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B14: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B15: See *
Note on B16: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B17: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B18: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B19: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B20: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B21: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B22: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B23: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B24: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B25: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B26: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B27: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B38: watts
Note on B39: watts
Note on F47: Enter your service voltage

## RCO #3
IBI Residential Load Calculation Worksheet | [8 empty] | Elect. Permit No.
Worksheet # 3
Revised 03/01/24
Conditions: Added wiring to an existing service in a single family dwelling.
(IE: Room addition, detached garage, hot tub, swimming pool, kitchen remodel, HVAC upgrade, etc.)
If sevice is upgraded, use worksheet 1 or 2. (Based on NEC 220.83)
Existing plus Added Loads (less HVAC)
|  | sq. ft. @ 3 watts sq. ft | [6 empty] | 0 | watts
|  | Small Appliance Circuits @ 1500 watts ea. (Minimum is two) | [6 empty] | 0 | watts
|  | Laundry Circuit(s) @ 1500 watts ea. (Minimum is one) | [6 empty] | 0 | watts
|  | Range (Nameplate Rating) | [6 empty] | 0 | watts
|  | Cooktop (Nameplate Rating) | [6 empty] | 0 | watts
|  | Oven (Nameplate Rating) | [6 empty] | 0 | watts
|  | Electric Water Heater | [6 empty] | 0 | watts
|  | Electric Clothes Dryer (Enter larger: 5000 watts or nameplate rating) | [6 empty] | 0 | watts
|  | Dishwasher | [6 empty] | 0 | watts
|  | Disposal | [6 empty] | 0 | watts
|  | Sump Pump | [6 empty] | 0 | watts
|  | Sewage Pump | [6 empty] | 0 | watts
|  | Water Pump | [6 empty] | 0 | watts
|  | Microwave Oven | [6 empty] | 0 | watts
|  | Garage Door Opener | [6 empty] | 0 | watts
|  | EVSE (Enter larger: 7200 watts or nameplate rating) | [6 empty] | 0 | watts
[9 empty] | 0 | watts
[9 empty] | 0 | watts
[9 empty] | 0 | watts
|  | Total Calculated Load (less HVAC) | [6 empty] | 0 | watts
HVAC Load
Compute the HVAC load and enter the LARGER of these air-conditioning or space heating loads.
| Air Conditioning Load (Volts X Amps = Watts) | [8 empty] | watts
Furnace/Air Handler (Volts X Amps = Watts)
OR
| Electric Space Heating Load (Volts X Amps = Watts) | [8 empty] | watts
(Central electric furnace, electric baseboard heaters, ceiling radiant heat, etc.)
OR
| Heat Pump with Central Electric Furnace (Volts X Amps = Watts) | [8 empty] | watts
(Nameplate rating of heat pump compressor plus electric furnace)
| HVAC Load | [7 empty] | 0 | watts
Service Demand
Total Computed Load (NEC 220.83)
|  | First 8kw of Total Calculated Load (less HVAC) @ 100% | [6 empty] | 0 | watts
|  | Remainder of Total Calculated Load (less HVAC) @ 40% | [6 empty] | 0 | watts
|  | HVAC Load @ 100% | [6 empty] | 0 | watts
|  | Calculated Service Load | [6 empty] | 0 | watts
| Calculated Service Load |  |  | ¸ | Service Voltage |  | = | Minimum Service Ampacity
| 0 |  | watts | ¸ | 240 | volts | = | 0 |  | amps
Note on A32: Only choose ONE of the THREE choices in STEP 4 Section
Note on A35: Only choose ONE of the THREE choices in STEP 4 Section
Note on A38: Only choose ONE of the THREE choices in STEP 4 Section
Note on B9: TOTAL sq. ft.
Note on B10: Number of
Note on B11: Number of
Note on B12: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B13: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B14: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B15: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B16: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B17: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B18: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B19: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B20: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B21: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B22: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B23: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B24: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B25: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B26: Nameplate Rating in watts (Volts x Amps = Watts)
Note on B27: Nameplate Rating in watts (Volts x Amps = Watts)
Note on J50: Enter your service voltage
Note on U32: Only enter value if Air Conditioning Load CLICK button is checked (far left)
Note on U33: Only enter value if Air Conditioning Load CLICK button is checked (far left)
Note on U35: Only enter value if Electric Space Heating Load CLICK button is checked (far left)
Note on U38: Only enter value if Heat Pump with Central Electric Furnace Load CLICK button is checked (far left)

## RCO #4
IBI Residential Load Calculation Worksheet | [10 empty] | Elect. Permit No.
Worksheet # 4
(Revised 01/09/08)
WORKSHEET BASED ON A STANDARD SERVICE CALCULATION
This Worksheet (NEC standard calculation Art. 220.1 through 220.61)
may be used for a single family, two-family, or three-family dwelling.
NOTE: This calculation must be used for two-family dwellings.
General Lighting Load
1 |  | sq. ft. @ 3 watts sq. ft (Total all units) | [8 empty] | 0 | watts
2 |  | Small Appliance Circuits @ 1500 watts ea. | [8 empty] | 0 | watts
(Minimum is 2 per unit)
3 |  | Laundry Circuit(s) @ 1500 watts ea. (Minimum is 1 per unit) | [8 empty] | 0 | watts
4 |  | Total lines 1, 2 & 3 | [8 empty] | 0 | watts
5 |  | First 3kw of Sub-total General Lighting Load (line 4 above) @ 100% | [8 empty] | 0 | watts
6 |  | Subtract line 5 from line 4 | [8 empty] | 0 | watts
7 |  | Enter 35% of line 6 | [8 empty] | 0 | watts
8 |  | Total lines 5 & 7 |  |  | TOTAL GENERAL LIGHTING LOAD | [5 empty] | 0 | watts
Range and Electric Clothes Dryer Load
Refer to the following to determine the range load. When using the Note*, substantiate your calculations using actual nameplate ratings on line 9. Enter the total range loads on line 10.
| one family | A. One range* (not over 12 KW rating each): Enter 8000 watts on line 10. | [9 empty] | watts
|  | B. One range* (over 12 KW rating each): Enter the sum of 8000 watts plus 400 watts for each KW that the range exceeds 12 KW on line 10. | [9 empty] | watts
| two family | C. Two ranges* (not over 12 KW rating each): Enter 11000 watts on line 10. | [9 empty] | watts
|  | D. Two ranges* (over 12 KW rating each): Enter the sum of 11000 watts plus 550 watts for each KW that the range exceeds 12 KW on line 10. | [9 empty] | watts
| three family | E. Three ranges* (not over 12 KW rating each): Enter 14000 watts on line 10. | [9 empty] | watts
|  | F. Three ranges* (over 12 KW rating each): Enter the sum of 14000 watts plus 700 for each KW that the range exceeds 12 KW on line 10. | [9 empty] | watts
*Note: For each dwelling unit, the load for a counter-mounted cooking unit and NOT more than TWO wall-mounted ovens may be calculated by adding the nameplate rating of the individual appliances and treating the total as the equivalent to one range.
9 | Calculations:
10 | TOTAL RANGE LOAD | [9 empty] | 0 | watts
To determine clothes dryer load - enter 5000 watts (or nameplate rating - whichever is larger) for each clothes dryer.
|  | Clothes Dryer(s) - Unit 1 | [9 empty] | watts
|  | Clothes Dryer(s) - Unit 2 | [9 empty] | watts
|  | Clothes Dryer(s) - Unit 3 | [9 empty] | watts
11 |  | TOTAL DRYER LOAD | [8 empty] | 0 | watts
12 |  | TOTAL RANGE AND DRYER LOAD | [8 empty] | 0 | watts
IBI Residential Load Calculation Worksheet | [10 empty] | Elect. Permit No.
Worksheet # 4 continued
(Revised 01/09/08)
FIXED APPLIANCE LOAD
(Appliances which are fastened in place).
Do not include electric ranges, clothes dryers, or HVAC equipment.
Include water heaters, disposals, dishwashers, trash compactors, microwave ovens, etc.
| TOTAL QTY | List each appliance load separately. (For two and three-family dwellings, list the quantity of each appliance and the sum of the nameplate ratings (in watts) separately):
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Fixed Appliances | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | SUB-TOTAL FIXED APPLIANCE LOAD | [8 empty] | 0 | watts
If there are three or less appliances in this section, enter the
Sub-Total Fixed Appliance Load on line 13.
If there are four or more appliances in this section, enter 75% of the
Sub-Total Fixed Appliance Load on line 13, use line below for calculating.
|  |  |  | * | 0.75 |  | = | 0
13 |  | TOTAL FIXED APPLIANCE LOAD | [9 empty] | watts
HVAC AND OTHER LOADS
| TOTAL QTY | All loads @ 100% (Volts X Amps = Watts)
|  | *Nameplate Heat Pump Compressor Loads | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | *Nameplate Electric Furnace Loads | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | *Nameplate Air-conditioning Loads | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | *Nameplate Blower Motor Loads | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
14 |  | TOTAL HVAC LOAD | [8 empty] | 0 | watts
* Where it is unlikely that two or more noncoincident loads will be used simultaneously, it shall be permissible to use only the LARGEST load(s) that will be used at one time for calculating the total load of the service.
IBI Residential Load Calculation Worksheet | [10 empty] | Elect. Permit No.
Worksheet # 4 continued
(Revised 01/09/08)
Other loads @ 100%
Examples are sump pumps, sewage pumps, whirlpool motors, attic fans, swimming pool equipment, garage door openers, etc.
| TOTAL QTY | List each appliance load separately. (For two and three-family dwellings, list the quantity of each and the sum of the nameplate ratings (in watts) separately):
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
|  | Other Load | [5 empty] | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  |  | Unit #3
15 |  | TOTAL OTHER LOADS | [8 empty] | 0 | watts
16 |  | HVAC and OTHER TOTAL LOADS | [8 empty] | 0 | watts
CALCULATE THE SERVICE LOAD
| TOTAL GENERAL LIGHTING LOAD | [8 empty] | 0 |  | watts
| TOTAL RANGE AND DRYER LOAD | [8 empty] | 0 |  | watts
| TOTAL FIXED APPLIANCE LOAD | [8 empty] | 0 |  | watts
| TOTAL HVAC AND OTHER LOADS | [8 empty] | 0 |  | watts
| TOTAL LOAD | [8 empty] | 0 |  | watts
| TOTAL LOAD |  |  | ¸ | Service Voltage |  |  |  | = | Minimum Service Ampacity
| 0 |  | watts | ¸ | 240 | volts |  |  | = | 0 |  | amps
Note on B12: TOTAL sq. ft. for ALL UNITS
Note on B13: # of ckts (TOTAL OF ALL UNITS)-Minimum of 2 per UNIT
Note on B15: # of ckts-Minimum of 1 per UNIT
Note on B48: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B50: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B52: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B54: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B56: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B58: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B60: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B62: Enter total quantity (ALL UNITS) of specific Fixed Appliance (shown at the right)
Note on B92: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B94: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B96: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B98: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B100: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B102: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B104: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on B106: Enter total quantity (ALL UNITS) of specific Other Load (shown at the right)
Note on C48: Name/List the Fixed Appliances indicated on this line
Note on C50: Name/List the Fixed Appliances indicated on this line
Note on C52: Name/List the Fixed Appliances indicated on this line
Note on C54: Name/List the Fixed Appliances indicated on this line
Note on C56: Name/List the Fixed Appliances indicated on this line
Note on C58: Name/List the Fixed Appliances indicated on this line
Note on C60: Name/List the Fixed Appliances indicated on this line
Note on C62: Name/List the Fixed Appliances indicated on this line
Note on C92: Name/List the Other Load indicated on this line
Note on C94: Name/List the Other Load indicated on this line
Note on C96: Name/List the Other Load indicated on this line
Note on C98: Name/List the Other Load indicated on this line
Note on C100: Name/List the Other Load indicated on this line
Note on C102: Name/List the Other Load indicated on this line
Note on C104: Name/List the Other Load indicated on this line
Note on C106: Name/List the Other Load indicated on this line
Note on E49: Enter appliance load in watts
Note on E51: Enter appliance load in watts
Note on E53: Enter appliance load in watts
Note on E55: Enter appliance load in watts
Note on E57: Enter appliance load in watts
Note on E59: Enter appliance load in watts
Note on E61: Enter appliance load in watts
Note on E63: Enter appliance load in watts
Note on E76: Enter load in watts
Note on E78: Enter load in watts
Note on E80: Enter load in watts
Note on E82: Enter load in watts
Note on E93: Enter Other Load - load in watts
Note on E95: Enter Other Load - load in watts
Note on E97: Enter Other Load - load in watts
Note on E99: Enter Other Load - load in watts
Note on E101: Enter Other Load - load in watts
Note on E103: Enter Other Load - load in watts
Note on E105: Enter Other Load - load in watts
Note on E107: Enter Other Load - load in watts
Note on J121: Enter Service voltage
Note on K49: Enter appliance load in watts
Note on K51: Enter appliance load in watts
Note on K53: Enter appliance load in watts
Note on K55: Enter appliance load in watts
Note on K57: Enter appliance load in watts
Note on K59: Enter appliance load in watts
Note on K61: Enter appliance load in watts
Note on K63: Enter appliance load in watts
Note on K76: Enter load in watts
Note on K78: Enter load in watts
Note on K80: Enter load in watts
Note on K82: Enter load in watts
Note on K93: Enter Other Load - load in watts
Note on K95: Enter Other Load - load in watts
Note on K97: Enter Other Load - load in watts
Note on K99: Enter Other Load - load in watts
Note on K101: Enter Other Load - load in watts
Note on K103: Enter Other Load - load in watts
Note on K105: Enter Other Load - load in watts
Note on K107: Enter Other Load - load in watts
Note on Q49: Enter appliance load in watts
Note on Q51: Enter appliance load in watts
Note on Q53: Enter appliance load in watts
Note on Q55: Enter appliance load in watts
Note on Q57: Enter appliance load in watts
Note on Q59: Enter appliance load in watts
Note on Q61: Enter appliance load in watts
Note on Q63: Enter appliance load in watts
Note on Q76: Enter load in watts
Note on Q78: Enter load in watts
Note on Q80: Enter load in watts
Note on Q82: Enter load in watts
Note on Q93: Enter Other Load - load in watts
Note on Q95: Enter Other Load - load in watts
Note on Q97: Enter Other Load - load in watts
Note on Q99: Enter Other Load - load in watts
Note on Q101: Enter Other Load - load in watts
Note on Q103: Enter Other Load - load in watts
Note on Q105: Enter Other Load - load in watts
Note on Q107: Enter Other Load - load in watts

## RCO #5
IBI Residential Load Calculation Worksheet | [9 empty] | Elect. Permit No.
Worksheet # 5
(Revised 01/09/08)
Worksheet using the NEC Optional Calculation for a 3-FAMILY Dwelling
(Based on NEC 220.84)
This optional calculation may be used for a three family dwelling if all of the following conditions are met:
(1.) No dwelling unit is supplied by more than one feeder.
(2.) Each dwelling unit is equipped with electric cooking equipment.
(See NEC 220.84 (A)(2) Exception if you want to use this optional calculation with gas cooking equipment)
(3.) Each dwelling unit is equipped with either electric space heating or air conditioning, or both.
STEP 1
(Required loads for dwelling units)
|  | sq. ft. @ 3 watts sq. ft (Total all units) | [7 empty] | 0 | watts
|  | Small Appliance Circuits @ 1500 watts ea. | [7 empty] | 0 | watts
(Minimum is 2 per unit)
|  | Laundry Circuit(s) @ 1500 watts ea. (Minimum is 1 per unit) | [7 empty] | 0 | watts
[10 empty] | 0 | watts
| TOTAL QTY | STEP 2
List All Appliance Loads (Nameplate Ratings in watts) (Volts X Amps = Watts):
|  | Ranges, Cooktops, Ovens |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Electric Water Heaters |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Electric Clothes Dryers - See * |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Gas Clothes Dryer Motors |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Dishwashers |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Disposals |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Appliances |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
[10 empty] | 0 | watts
(* Electric dryers use 5000 watts each or nameplate ratings, total of all units )
IBI Residential Load Calculation Worksheet | [9 empty] | Elect. Permit No.
Worksheet # 5 continued
(Revised 01/09/08)
STEP 3
List All Other Loads (Nameplate Ratings - in watts) (Volts X Amps = Watts):
| TOTAL QTY | (Examples: Whirlpool motors, attic fans, garage door openers, swimming pool equipment, sump pumps, etc.)
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
|  | Other Load |  |  |  |  | TOTAL of ALL units |  |  | 0 | watts
|  | Unit #1 |  | Unit #2 |  |  |  | Unit #3
[10 empty] | 0 | watts
STEP 4
Compute the HVAC load and enter the LARGER of these air-conditioning or space heating loads.
ENTER TOTAL OF ALL UNITS:
| Air Conditioning Load (Volts X Amps = Watts) | [9 empty] | watts
(Combined nameplate ratings of ALL A/C compressors plus ALL blower motors)
OR
| Electric Space Heating Load (Volts X Amps = Watts) | [9 empty] | watts
(ALL central electric furnaces, electric baseboard heaters, ceiling radiant heat, etc.)
OR
| Heat Pump with Central Electric Furnace (Volts X Amps = Watts) | [9 empty] | watts
(Combined nameplate ratings of ALL heat pump compressors plus ALL electric furnaces)
| Total HVAC Load (all units) | [8 empty] | 0 | watts
IBI Residential Load Calculation Worksheet | [9 empty] | Elect. Permit No.
Worksheet # 5 continued
(Revised 01/09/08)
STEP 5
| Enter total of all loads as determined by Steps 1 through 4 | [7 empty] | 0 |  | watts
STEP 6
Compute the minimum size service required:
| Total Watts (from step 5) |  |  | ¸ | Service Voltage |  |  | = | Total Amps
| 0 |  | watts | ¸ | 240 | volts |  | = | 0 |  | amps
Multiply Total Amps by 0.45 (45%) =
| Total Amps |  |  | * | 0.45 percent (45%) |  |  | = | Dwelling Units Demand Amps
| 0 |  | amps | * | 0.45 |  |  | = | 0 |  | amps
STEP 7
| Enter “House Loads” in amperes: | [9 empty] | amps
(House Loads, if any, shall be calculated in accordance with Part III of NEC 220)
Describe house loads in the space provided below.
Compute the minimum size service required:
| Dwelling Units Demand Amps |  |  | + | House Load Amps |  |  | = | Minimum Service Ampacity
| 0 |  | amps | + | 0 |  |  | = | 0 |  | amps
Note on A84: Only choose ONE of the THREE choices in STEP 4 Section
Note on A87: Only choose ONE of the THREE choices in STEP 4 Section
Note on A90: Only choose ONE of the THREE choices in STEP 4 Section
Note on B16: TOTAL sq. ft. for ALL UNITS
Note on B17: # of ckts-Minimum of 2 per UNIT
Note on B19: # of ckts-Minimum of 1 per UNIT
Note on B24: Enter total quantity (ALL UNITS) of Ranges, Cooktops, Ovens
Note on B26: Enter total quantity (ALL UNITS) of Electric Water Heaters
Note on B28: Enter total quantity (ALL UNITS) of Electric Clothes Dryers
Note on B30: Enter total quantity (ALL UNITS) of Gas Clothes Dryer Motors
Note on B32: Enter total quantity (ALL UNITS) of Dishwashers
Note on B34: Enter total quantity (ALL UNITS) of Disposals
Note on B36: Enter total quantity (ALL UNITS) of Other Appliances
Note on B38: Enter total quantity (ALL UNITS) of Other Appliances
Note on B40: Enter total quantity (ALL UNITS) of Other Appliances
Note on B42: Enter total quantity (ALL UNITS) of Other Appliances
Note on B44: Enter total quantity (ALL UNITS) of Other Appliances
Note on B46: Enter total quantity (ALL UNITS) of Other Appliances
Note on B48: Enter total quantity (ALL UNITS) of Other Appliances
Note on B59: Enter total quantity (ALL UNITS) of Other Load
Note on B61: Enter total quantity (ALL UNITS) of Other Load
Note on B63: Enter total quantity (ALL UNITS) of Other Load
Note on B65: Enter total quantity (ALL UNITS) of Other Load
Note on B67: Enter total quantity (ALL UNITS) of Other Load
Note on B69: Enter total quantity (ALL UNITS) of Other Load
Note on B71: Enter total quantity (ALL UNITS) of Other Load
Note on B73: Enter total quantity (ALL UNITS) of Other Load
Note on B75: Enter total quantity (ALL UNITS) of Other Load
Note on B77: Enter total quantity (ALL UNITS) of Other Load
Note on C36: Name/List the Other Appliances indicated on this line
Note on C38: Name/List the Other Appliances indicated on this line
Note on C40: Name/List the Other Appliances indicated on this line
Note on C42: Name/List the Other Appliances indicated on this line
Note on C44: Name/List the Other Appliances indicated on this line
Note on C46: Name/List the Other Appliances indicated on this line
Note on C48: Name/List the Other Appliances indicated on this line
Note on C59: Name/List the Other Load indicated on this line
Note on C61: Name/List the Other Load indicated on this line
Note on C63: Name/List the Other Load indicated on this line
Note on C65: Name/List the Other Load indicated on this line
Note on C67: Name/List the Other Load indicated on this line
Note on C69: Name/List the Other Load indicated on this line
Note on C71: Name/List the Other Load indicated on this line
Note on C73: Name/List the Other Load indicated on this line
Note on C75: Name/List the Other Load indicated on this line
Note on C77: Name/List the Other Load indicated on this line
Note on E25: Enter load in watts
Note on E27: Enter load in watts
Note on E29: Enter load in watts
Note on E31: Enter load in watts
Note on E33: Enter load in watts
Note on E35: Enter load in watts
Note on E37: Enter load in watts
Note on E39: Enter load in watts
Note on E41: Enter load in watts
Note on E43: Enter load in watts
Note on E45: Enter load in watts
Note on E47: Enter load in watts
Note on E49: Enter load in watts
Note on E60: Enter load in watts
Note on E62: Enter load in watts
Note on E64: Enter load in watts
Note on E66: Enter load in watts
Note on E68: Enter load in watts
Note on E70: Enter load in watts
Note on E72: Enter load in watts
Note on E74: Enter load in watts
Note on E76: Enter load in watts
Note on E78: Enter load in watts
Note on J111: Enter Service voltage
Note on K25: Enter load in watts
Note on K27: Enter load in watts
Note on K29: Enter load in watts
Note on K31: Enter load in watts
Note on K33: Enter load in watts
Note on K35: Enter load in watts
Note on K37: Enter load in watts
Note on K39: Enter load in watts
Note on K41: Enter load in watts
Note on K43: Enter load in watts
Note on K45: Enter load in watts
Note on K47: Enter load in watts
Note on K49: Enter load in watts
Note on K60: Enter load in watts
Note on K62: Enter load in watts
Note on K64: Enter load in watts
Note on K66: Enter load in watts
Note on K68: Enter load in watts
Note on K70: Enter load in watts
Note on K72: Enter load in watts
Note on K74: Enter load in watts
Note on K76: Enter load in watts
Note on K78: Enter load in watts
Note on Q25: Enter load in watts
Note on Q27: Enter load in watts
Note on Q29: Enter load in watts
Note on Q31: Enter load in watts
Note on Q33: Enter load in watts
Note on Q35: Enter load in watts
Note on Q37: Enter load in watts
Note on Q39: Enter load in watts
Note on Q41: Enter load in watts
Note on Q43: Enter load in watts
Note on Q45: Enter load in watts
Note on Q47: Enter load in watts
Note on Q49: Enter load in watts
Note on Q60: Enter load in watts
Note on Q62: Enter load in watts
Note on Q64: Enter load in watts
Note on Q66: Enter load in watts
Note on Q68: Enter load in watts
Note on Q70: Enter load in watts
Note on Q72: Enter load in watts
Note on Q74: Enter load in watts
Note on Q76: Enter load in watts
Note on Q78: Enter load in watts
Note on U84: Only enter value if Air Conditioning Load CLICK button is checked (far left)
Note on U87: Only enter value if Electric Space Heating Load CLICK button is checked (far left)
Note on U90: Only enter value if Heat Pump with Central Electric Furnace Load CLICK button is checked (far left)